# PTH Sensor – Setup & Testing Guide

Nautilus board (STM32H723ZG)  ·  Waveshare Modbus RTU Analog Input 8CH  ·  4-20mA Temperature/Humidity transmitter

Project: nautilus_PTH_test

# 1. Overview

The PTH transmitter provides two 4-20mA current-loop outputs (temperature and humidity). These are read by a Waveshare 8-channel analog input module, which exposes the values over Modbus RTU on an RS485 bus. The Nautilus board reads the module over USART2 (RS485) and prints detailed data and a test menu over USART3 (the ST-Link virtual COM port).

PTH sensor (2x 4-20mA)  ->  Waveshare 8CH (current in)  ->  RS485/Modbus  ->  STM32H723 USART2 (DE=PE4)

Debug / test console: USART3 @ 115200 8N1 (ST-Link VCP).

# 2. Firmware files added

| File | Purpose |
| --- | --- |
| Core/Inc/pth_sensor.h | Configuration (ranges, channels, address) and public API |
| Core/Src/pth_sensor.c | Modbus-RTU driver, 4-20mA conversion, detailed debug, test console |
| Core/Src/main.c | Three hooks inside USER CODE blocks: include, PTH_Init(&huart2,&huart3), PTH_Task() in the main loop |

All main.c changes are inside CubeMX USER CODE markers, so they survive code regeneration. Floats are formatted with integer math, so no linker flags are required.

# 3. Physical hardware setup

## 3.1  Power (one 24 V DC supply for both)

Use a 24 V DC supply (within the sensor’s 10-30 V range; the Waveshare module accepts 7-36 V).

•  PSU +  →  sensor V+  and  Waveshare VIN

•  PSU −  →  sensor V−/GND  and  Waveshare GND

•  Also tie PSU GND → Nautilus board GND  (shared reference for RS485 and the current loops).

## 3.2  Sensor 4-20mA outputs → Waveshare channels

Identify the two current outputs from the sensor label/datasheet (wire colours vary).

•  Humidity 4-20mA output  →  Waveshare CH1 input

•  Temperature 4-20mA output  →  Waveshare CH2 input

•  The loop current returns through the shared GND.

IMPORTANT: Set Waveshare CH1 & CH2 to CURRENT (0-20mA) mode – usually a per-channel jumper (voltage vs current). If left in voltage mode the readings are meaningless.

## 3.3  RS485 to the Nautilus board (via the shield)

•  Waveshare A+  →  board RS485 A

•  Waveshare B−  →  board RS485 B

•  Waveshare GND  →  board GND

•  If you only get TIMEOUTs, swap A/B  (the most common RS485 mistake).

•  Long/noisy bus: 120 Ω across A-B at each end (Waveshare has a termination jumper).

## 3.4  Module address / baud

Factory default is address 1, 9600 8N1, which matches the firmware. If different, change the address at runtime with the console command "addr <n>", or reconfigure the module.

# 4. Build, flash, and open the console

1. In CubeIDE select nautilus_PTH_test, press F5 (Refresh), then Project → Build. CubeIDE auto-adds pth_sensor.c to the build on refresh.

2. Flash with Run ▶ (or Debug).

3. On the NUCLEO-H723ZG, USART3 is the ST-Link Virtual COM Port – no extra USB-serial adapter needed.

4. Open a serial terminal (PuTTY / Tera Term / CubeIDE) on the ST-Link VCP COM port at 115200 8N1. The banner and menu appear.

# 5. Interactive test console commands

Type a command and press Enter.

| Command | Action |
| --- | --- |
| read | One detailed reading (raw hex, mA, % of span, engineering value, status) |
| cont / stop | Start / stop continuous polling |
| scan | Dump raw values of all 8 channels – helps find which channel is wired |
| dump | Show last Modbus TX/RX frames in hex |
| verbose <0-2> | 0 quiet, 1 normal, 2 adds TX/RX frame hex to every reading |
| mode ua ¦ raw | Flip raw-register interpretation (micro-amps vs 0-4095 counts) |
| temp <lo> <hi> | Set temperature range mapped to 4-20mA (degC) |
| hum <lo> <hi> | Set humidity range mapped to 4-20mA (%RH) |
| ch <hum> <tmp> | Remap which Waveshare channels are humidity / temperature (0-7) |
| addr <n> | Set Modbus slave address (1-247) |
| rate <ms> | Continuous poll period |
| cfg | Write 4-20mA data-type to both channels (optional, module dependent) |
| cfgshow | Print current configuration |
| ? | Full help |

Example detailed output line:

TEMP (ch1)  raw=0x2EE0 (12000)  12.000 mA  span=50.0%  => 20.00 degC  [OK]

LEDs: green = both channels good, red = any fault, status LED toggles on each read.

# 6. Three things to confirm on the bench

1.  Engineering ranges. Defaults are -40..80 degC and 0..100 %RH. Read the true ranges from the datasheet and set them with the temp / hum commands. This only affects the final number, not comms.

2.  Channel mapping. Run scan, then breathe on the sensor: the humidity channel’s mA rises. Swap with the ch command if needed.

3.  Scale mode. Default assumes the module returns current in micro-amps (4-20mA -> 4000..20000). If a 4-20mA input shows raw ~2400-12000, mode ua is correct; if it shows ~800-4095, use mode raw. The scan command shows this immediately.

# 7. Troubleshooting

| Symptom | Likely cause / fix |
| --- | --- |
| TIMEOUT (no reply) | Swap RS485 A/B; check slave address (addr); wrong baud; module unpowered; DE wiring |
| UNDER-RANGE (<3.5 mA) | Sensor not powered, open loop, or wrong channel |
| OVER-RANGE (>21 mA) | Short circuit or miswire on the loop |
| CRC error | Electrical noise; add 120 ohm termination; shorten cable; check grounding |
| Numbers look wrong | Wrong scale (mode ua/raw); channel in voltage mode not current; wrong engineering range |
| Values swapped | Temperature and humidity channels reversed – use ch <hum> <tmp> |